## CALCULATIONS
CABLE CURRENT RATINGS & SELECTION - IEC 60364 / BS 7671
CABLE SIZING CALCULATOR
LOAD PARAMETERS |  |  | DERATING FACTORS
Load Power (kW): | 25 |  | Ambient Temp (°C): | 35
Voltage (V): | 415 |  | Grouping Factor: | 0.8
Power Factor: | 0.85 |  | Installation Method: | Method C
Circuit Type: | 3-Phase |  | Total Derating: | 0.752
Load Current (A): | 40.9178 |  | Design Current (A): | 54.412
CABLE CURRENT RATINGS (PVC/XLPE)
Size (mm²) | Method A | Method B | Method C | Method D | Method E | Typical CB (A)
1.5 | 13.5 | 13 | 17.5 | 18 | 22 | 10
2.5 | 18.5 | 18 | 24 | 25 | 30 | 16
4 | 25 | 24 | 32 | 34 | 40 | 25
6 | 32 | 31 | 41 | 43 | 52 | 32
10 | 44 | 42 | 57 | 60 | 71 | 50
16 | 59 | 56 | 76 | 80 | 96 | 63
25 | 77 | 73 | 99 | 106 | 119 | 80
35 | 96 | 89 | 121 | 131 | 148 | 100
50 | 117 | 108 | 147 | 162 | 180 | 125
70 | 150 | 136 | 188 | 209 | 232 | 160
95 | 182 | 164 | 227 | 255 | 282 | 200
120 | 210 | 188 | 262 | 297 | 328 | 250
150 | 240 | 216 | 300 | 344 | 379 | 315
185 | 273 | 245 | 341 | 394 | 434 | 400
240 | 321 | 286 | 400 | 467 | 514 | 500
300 | 367 | 328 | 458 | 540 | 593 | 630
SELECTED CABLE SIZE
Required Size (mm²): | 10
Circuit Breaker (A): | 50
VOLTAGE DROP CALCULATIONS
VOLTAGE DROP CALCULATOR |  |  | VOLTAGE DROP VALUES (mV/A/m)
|  |  | Cable Size | 3-Phase | Single Phase
Cable Length (m): | 50 |  | 1.5 | 29 | 31
Load Current (A): | 40.9178 |  | 2.5 | 18 | 19
Cable Size (mm²): | 16 |  | 4 | 11 | 12
System Voltage (V): | 415 |  | 6 | 7.3 | 7.9
mV/A/m (from table): | 2.4 |  | 10 | 4.4 | 4.7
Voltage Drop (V): | 4.9101 |  | 16 | 2.8 | 2.9
Voltage Drop (%): | 1.1832 |  | 25 | 1.75 | 1.85
Max Allowed (%): | 4 |  | 35 | 1.25 | 1.35
Status: | OK |  | 50 | 0.93 | 0.99
|  |  | 70 | 0.63 | 0.67
|  |  | 95 | 0.46 | 0.49
|  |  | 120 | 0.36 | 0.39
ELECTRICAL LOAD ESTIMATION & DIVERSITY
LOAD SCHEDULE
Load Description | Qty | Unit Load (kW) | Total Load (kW) | Diversity Factor | Diversified Load (kW)
Lighting - Office | 50 | 0.04 | 2 | 0.9 | 1.8
Lighting - Corridor | 20 | 0.04 | 0.8 | 0.8 | 0.64
Socket Outlets | 100 | 0.3 | 30 | 0.4 | 12
Air Conditioning | 10 | 3.5 | 35 | 0.8 | 28
Computers | 50 | 0.3 | 15 | 0.7 | 10.5
Printers | 10 | 0.5 | 5 | 0.3 | 1.5
Water Heaters | 5 | 3 | 15 | 0.4 | 6
Elevators | 2 | 15 | 30 | 1 | 30
Water Pumps | 3 | 7.5 | 22.5 | 0.6 | 13.5
Kitchen Equipment | 1 | 20 | 20 | 0.7 | 14
TOTAL CONNECTED LOAD (kW): |  |  | 175.3
MAXIMUM DEMAND (kW): |  |  |  |  | 117.94
OVERALL DIVERSITY FACTOR: |  |  |  |  | 0.67279
GENERATOR SIZING
Maximum Demand (kW): | 117.94
Power Factor: | 0.8
Generator kVA: | 147.425
Safety Factor: | 1.25
Selected Generator (kVA): | 190
POWER FACTOR CORRECTION CALCULATIONS
POWER FACTOR CORRECTION |  |  | COST SAVINGS ANALYSIS
Active Power (kW): | 100 |  | Monthly Energy (kWh): | 50000
Current PF: | 0.7 |  | Energy Rate (UGX/kWh): | 796
Target PF: | 0.95 |  | PF Penalty (%): | 20
Current Reactive Power (kVAr): | 102.0204 |  | Monthly Penalty (UGX): | 7960000
Target Reactive Power (kVAr): | 32.8684 |  | Annual Savings (UGX): | 95520000
Capacitor Bank Required (kVAr): | 69.152
Standard Bank Size (kVAr): | 70
ELECTRICAL PROTECTION & COORDINATION
SHORT CIRCUIT CALCULATIONS |  |  | EARTHING SYSTEM DESIGN
Transformer Rating (kVA): | 500 |  | Soil Resistivity (Ω·m): | 100
Impedance (%): | 4 |  | Rod Length (m): | 3
Secondary Voltage (V): | 415 |  | Rod Diameter (mm): | 16
Full Load Current (A): | 695.6027 |  | Single Rod Resistance (Ω): | 35.1206
Short Circuit Current (kA): | 17.3901 |  | Target Resistance (Ω): | 10
Breaking Capacity Required: | 25kA |  | Rods Required: | 4
SOLAR PV SYSTEM SIZING
SOLAR SYSTEM CALCULATOR |  |  | BATTERY BANK SIZING
Daily Energy Requirement (kWh): | 20 |  | Days of Autonomy: | 2
Peak Sun Hours: | 5.5 |  | Battery Voltage (V): | 48
System Efficiency (%): | 80 |  | Depth of Discharge (%): | 50
Panel Wattage (W): | 550 |  | Battery Efficiency (%): | 85
Required PV Power (kW): | 4.5455 |  | Battery Capacity (Ah): | 1960.7843
Number of Panels: | 9 |  | Battery Rating (Ah): | 200
Total Array Power (kW): | 4.95 |  | Batteries Required: | 10
UPS SYSTEM SIZING & BATTERY CALCULATIONS
UPS SIZING CALCULATOR
Critical Load (kW): | 10
Power Factor: | 0.8
Backup Time (min): | 30
UPS Efficiency (%): | 92
UPS Rating (kVA): | 15.625
Battery Power (kW): | 10.8696
Battery Energy (kWh): | 5.4348
Battery Bank Voltage (V): | 384
Battery Capacity (Ah): | 14.1531

## CODES
UGANDA ELECTRICAL STANDARDS - CABLES, RATINGS & PROTECTION
CABLE CURRENT RATINGS - IEC 60364 / BS 7671
Cable Size (mm²) | Installation Method A | Installation Method B | Installation Method C | Installation Method D | Installation Method E | Typical CB Size (A) | Notes
1.5 | 13.5 | 13 | 13 | 11.5 | 12 | 10-13 | Min size for fixed wiring
2.5 | 18 | 16 | 17 | 15 | 16 | 16 | Standard power circuits
4 | 24 | 21 | 23 | 20 | 21 | 20 | Heavy duty power
6 | 31 | 26 | 30 | 25 | 27 | 25 | Small equipment
10 | 42 | 36 | 40 | 34 | 37 | 32 | Standard sub-mains
16 | 56 | 46 | 51 | 43 | 47 | 40-50 | Large equipment
25 | 73 | 61 | 68 | 58 | 64 | 63 | Sub-distribution
35 | 89 | 75 | 84 | 71 | 79 | 80 | Main distribution
50 | 108 | 92 | 99 | 86 | 96 | 80-100 | Heavy sub-mains
70 | 136 | 116 | 119 | 103 | 116 | 100-125 | Large sub-mains
95 | 164 | 141 | 144 | 125 | 141 | 125-160 | Main feeders
120 | 192 | 164 | 171 | 149 | 169 | 160 | Large feeders
150 | 219 | 188 | 196 | 172 | 195 | 160-200 | Main risers
185 | 263 | 226 | 238 | 209 | 237 | 200-250 | Heavy feeders
240 | 308 | 264 | 276 | 244 | 278 | 250-315 | Large risers
300 | 354 | 304 | 328 | 290 | 330 | 315 | Main incoming
400 | 423 | 364 | 382 | 341 | 390 | 315-400 | Large incoming
500 | 486 | 420 | 440 | 394 | 450 | 400-500 | Very large loads
Installation Methods:
A: Method A1/A2 (Enclosed - insulated)
B: Method B1/B2 (Enclosed - on wall)
C: Method C (Clipped direct)
D: Method D1/D2 (Tray/ladder)
E: Method E (Free air)
COMPREHENSIVE ELECTRICAL FORMULAS - IEC 60364 / BS 7671
Formula Category | Formula Name | Formula | Variables | Notes | Example
Single Phase Power | Power (Real) | P = V × I × PF | P=Power(W), V=Voltage(V), I=Current(A), PF=Power Factor | Real power consumed | P = 230 × 10 × 0.8 = 1,840W
Single Phase Power | Power (Apparent) | S = V × I | S=Apparent Power(VA) | Total power including reactive | S = 230 × 10 = 2,300VA
Single Phase Power | Power (Reactive) | Q = V × I × sin(φ) | Q=Reactive Power(VAR), φ=Power angle | Non-working power | Q = S × sin(arccos(PF))
Single Phase Current | Current Calculation | I = P / (V × PF) |  | Design current from power | I = 2000 / (230 × 0.8) = 10.87A
Three Phase Power | Power (Real) - Balanced | P = √3 × V × I × PF | V=Line voltage(V) | Balanced 3-phase load | P = 1.732 × 400 × 10 × 0.8 = 5,542W
Three Phase Power | Power (Apparent) | S = √3 × V × I |  | Total apparent power | S = 1.732 × 400 × 10 = 6,928VA
Three Phase Current | Current Calculation | I = P / (√3 × V × PF) |  | Line current from power | I = 10000 / (1.732 × 400 × 0.8) = 18.04A
Cable Sizing | Minimum Cable Size | Iz ≥ Ib / (Ca × Cg × Ci × Cc) | Iz=Cable rating, Ib=Design current, Ca=Ambient, Cg=Grouping, Ci=Insulation, Cc=BS 7671 correction factors | Apply all correction factors
Cable Sizing | Design Current | Ib = Pd / (V × PF) | Pd=Design power load | Before diversity
Voltage Drop | Voltage Drop (Single Phase) | Vd = 2 × I × L × (R × cos(φ) + X × sin(φ)) / 1000 | Vd=Drop(V), L=Length(m), R=Resistance(mΩ/m), X=Reactance(mΩ/m) | IEC 60364-5-52 | Max 3% lighting, 5% power
Voltage Drop | Voltage Drop (Three Phase) | Vd = √3 × I × L × (R × cos(φ) + X × sin(φ)) / 1000
Voltage Drop | Voltage Drop % | Vd% = (Vd / V) × 100 |  | Must be ≤3% (lighting) or ≤5% (power)
Voltage Drop | Simplified (Single Phase) | Vd = (2 × I × L × R) / 1000 |  | For PF≈1 (resistive loads)
Short Circuit | Fault Level | Isc = V / (Zs) | Isc=Short circuit current(A), Zs=Impedance(Ω) | Earth fault loop impedance
Short Circuit | Let Through Energy | I²t = Isc² × t | t=Disconnection time(s) | For cable thermal withstand
Earthing | Earth Electrode Resistance | R = ρ × L / (2 × π × L) | ρ=Soil resistivity(Ωm), L=Rod length(m) | For vertical earth rod | Uganda: ρ≈50-200 Ωm
Earthing | Touch Voltage | Vtouch = 50 + (1.5 × ρs) / √t | ρs=Surface layer resistivity, t=Time(s) | IEC 61201 max permissible | 50V for t>1s
Load Calculation | Maximum Demand | MD = ΣPi × Di | MD=Maximum Demand, Pi=Load i, Di=Diversity factor | After diversity applied
Load Calculation | Diversity Factor | DF = Σ(Pi × DFi) / ΣPi | DFi=Individual diversity | Weighted average | See diversity table
Efficiency | Motor Efficiency | η = Pout / Pin × 100% | η=Efficiency, Pout=Mechanical output, Pin=Electrical input | Typical 85-95% for IE3/IE4
Efficiency | Transformer Efficiency | η = Pout / (Pout + Pcore + Pcopper) × 100% |  | Typical >98% at rated load
Power Factor | Power Factor | PF = P / S = cos(φ) | φ=Phase angle | Leading or lagging | Target: PF≥0.95
Power Factor | Required Capacitance | Qc = P × (tan(φ1) - tan(φ2)) | Qc=Capacitive VAR needed, φ1=Original PF, φ2=Target PF | PF correction
Harmonics | THD (Current) | THDi = √(Σ(In²)) / I1 × 100% | In=nth harmonic current, I1=Fundamental | IEEE 519 limits | Limit: <15% @ PCC
Illumination | Lumens | F = E × A / (MF × UF) | F=Lumens required, E=Illuminance(lux), A=Area(m²), MF=Maintenance factor, UF=Utilization factor | Lighting design | Office: 500 lux
Illumination | Number of Luminaires | N = F / (Ll × n) | N=Number, Ll=Lumens per luminaire, n=Lamps per luminaire
Battery Backup | Battery Capacity (Ah) | Ah = (P × t) / (V × η × DoD) | P=Load(W), t=Time(hr), V=Voltage, η=Efficiency, DoD=Depth of Discharge | UPS/emergency power | DoD typically 0.8
UGANDA-SPECIFIC REQUIREMENTS & LOCAL STANDARDS
Category | Requirement | Authority | Specification | Notes
Electrical Installation | Wiring Regulations Compliance | ERA (Electricity Regulatory Authority) | IEC 60364 / BS 7671 | Mandatory for all installations
Electrical Installation | Installation Certificate | ERA | Form ERA/ELE/01 | Required before energization
Electrical Installation | Testing & Commissioning Report | ERA | IEC 60364-6 | Insulation resistance, earth loop, RCD tests
Voltage Standards | Single Phase Supply | UMEME/ERA | 230V ±10% @ 50Hz | Actual range: 207-253V
Voltage Standards | Three Phase Supply | UMEME/ERA | 400V ±10% @ 50Hz | Actual range: 360-440V
Voltage Standards | Frequency Tolerance | ERA | 50Hz ±1% | 49.5-50.5Hz acceptable
Earthing | Main Earthing Conductor | ERA | Min 16mm² copper | TN-S or TN-C-S system
Earthing | Earth Electrode Resistance | ERA/KCCA | ≤5Ω (LV), ≤1Ω (HV) | Measured at dry season
Earthing | Soil Resistivity (Uganda) | Typical Range | 50-200 Ωm | Varies by location, clay/laterite soil
Lightning Protection | Risk Assessment | KCCA/IEC 62305 | IEC 62305-2 | Required for buildings >15m or public occupancy
Lightning Protection | Protection Level | IEC 62305 | Class II (Normal) | Class I for critical facilities
Generator Installation | Noise Limits | NEMA | ≤70dB(A) @ 1m daytime, ≤55dB(A) night | NEA Cap 153
Generator Installation | Emission Standards | NEMA | EPA Tier 2/3 | Environmental compliance required
Generator Installation | Fuel Storage | NEMA/KCCA | Min 2hr bund capacity | Double-wall tanks preferred
Generator Installation | ATS Changeover Time | Uganda Practice | ≤15 seconds | Critical: ≤5 seconds
Solar PV | Net Metering Regulations | ERA | ERA Solar PV Regulations 2023 | Up to 5MW for grid connection
Solar PV | Feed-in Tariff | ERA | Published rates | Check ERA website for current rates
Cable Sizing | Minimum Conductor Size (Fixed) | BS 7671/ERA | 1.5mm² (lighting), 2.5mm² (power) | Fixed wiring minimum
Cable Sizing | Volt Drop Limit | BS 7671 | 3% (lighting), 5% (power) | From origin to final circuit
Protective Devices | RCD Protection | BS 7671 | 30mA for sockets ≤32A | All socket outlets require RCD
Protective Devices | Circuit Breaker Standards | ERA | IEC 60898 (MCB), IEC 60947 (MCCB) | Type B/C for general use
Metering | Accuracy Class | ERA | Class 1 (Active), Class 2 (Reactive) | IEC 62053 standards
Metering | Meter Installation | UMEME | External weatherproof box | Customer accessible, sealed by utility
Emergency Power | Critical Facilities | Fire Code/MOH | 100% backup capacity | Hospitals, data centers
Emergency Power | Backup Duration | Standard Practice | 4-8 hours minimum | Based on grid reliability
Inspection | Periodic Inspection Interval | ERA | 5 years (domestic), 3 years (commercial) | Or after major alteration
Documentation | As-Built Drawings | KCCA | Required format: ISO 19650 | For building permit closure
Documentation | O&M Manuals | Client Standard | Mandatory | English language, equipment datasheets
Tariffs | Commercial Tariff (C1) | UMEME | Demand + Energy charges | Check current published rates
Tariffs | Industrial Tariff (M1-M3) | UMEME | Demand + Energy + PF penalty | PF<0.9 attracts penalty
Safety | Isolation Distance (LV) | IEC 61936 | ≥2.5m | From overhead lines to building
Safety | Clearance Height (LV) | ERA | ≥6m (road crossing), ≥4m (other) | Above ground level
Enclosure Rating | Minimum IP Rating (Outdoor) | IEC 60529 | IP54 | Dust/water ingress protection
Enclosure Rating | Minimum IP Rating (Indoor) | IEC 60529 | IP20 | General indoor use
CABLE DERATING FACTORS
AMBIENT TEMPERATURE CORRECTION FACTORS
Ambient Temp (°C) | PVC Insulation (70°C) | XLPE Insulation (90°C) | Silicone Insulation (180°C)
25 | 1.03 | 1.04 | 1.04
30 | 1 | 1 | 1
35 | 0.94 | 0.96 | 0.97
40 | 0.87 | 0.91 | 0.94
45 | 0.79 | 0.87 | 0.92
50 | 0.71 | 0.82 | 0.89
55 | 0.61 | 0.76 | 0.86
60 | 0.5 | 0.71 | 0.84
GROUPING CORRECTION FACTORS
Number of Circuits | Touching / Bunched | Single Layer on Wall | Single Layer Clipped
1 | 1 | 1 | 1
2 | 0.8 | 0.85 | 0.9
3 | 0.7 | 0.79 | 0.85
4 | 0.65 | 0.75 | 0.8
5 | 0.6 | 0.73 | 0.78
6 | 0.57 | 0.72 | 0.76
7 | 0.54 | 0.72 | 0.73
8 | 0.52 | 0.71 | 0.71
9 | 0.5 | 0.7 | 0.7
10 | 0.48 | 0.7 | 0.7
11-15 | 0.45 | 0.68 | 0.68
16-20 | 0.41 | 0.66 | 0.66
DIVERSITY AND DEMAND FACTORS
Load Type | Diversity Factor | Typical Power Factor | Application | Standard Reference
Lighting - Office | 0.9 | 0.95 | General office lighting | BS 7671
Lighting - Corridor | 1 | 0.95 | Emergency route lighting | BS 7671
Lighting - External | 1 | 0.9 | External/security lighting | IEC 60364
Power Outlets - Office | 0.4 | 0.85 | Desktop equipment | BS 7671
Power Outlets - Kitchen | 0.6 | 0.85 | Small appliances | BS 7671
Power Outlets - Workshop | 0.75 | 0.85 | Power tools | IEC 60364
HVAC - Air Conditioning | 1 | 0.85 | Cooling systems | ASHRAE
HVAC - Ventilation | 1 | 0.85 | Exhaust/supply fans | IEC 60364
Motors - Continuous | 1 | 0.8 | Pumps, compressors | IEC 60034
Motors - Intermittent | 0.75 | 0.8 | Occasional use | IEC 60034
Water Heaters | 1 | 1 | Resistive heating | IEC 60364
Elevators/Lifts | 1 | 0.7 | Vertical transport | ISO 4190
Kitchen Equipment | 0.8 | 0.9 | Commercial kitchen | BS 7671
IT/Server Rooms | 1 | 0.95 | Data center loads | TIA-942
Special Equipment | 0.8 | 0.85 | Case-by-case assessment | Engineering judgment
STANDARD CIRCUIT BREAKER RATINGS (IEC 60898 / IEC 60947)
Rating (A) | Type | Trip Curves | Breaking Capacity (kA) | Typical Application | Voltage
6 | MCB | B, C | 6, 10 | Lighting circuits | 230V
10 | MCB | B, C | 6, 10 | Small appliances | 230V
16 | MCB | B, C, D | 6, 10 | Power circuits | 230V
20 | MCB | C, D | 6, 10 | Heavy duty sockets | 230V
25 | MCB | C, D | 6, 10 | Sub-distribution | 230V
32 | MCB | C, D | 10 | Large equipment | 230/400V
40 | MCB | C, D | 10 | Sub-mains | 400V
50 | MCB | C, D | 10, 15 | Distribution | 400V
63 | MCB | C, D | 10, 15 | Small sub-mains | 400V
80 | MCB/MCCB | C, D | 15, 25 | Large sub-mains | 400V
100 | MCB/MCCB | C, D | 15, 25 | Distribution boards | 400V
125 | MCCB | C | 25, 36 | Main distribution | 400V
160 | MCCB | C | 25, 36 | Large feeders | 400V
200 | MCCB | C | 36, 50 | Main risers | 400V
250 | MCCB | C | 36, 50 | Heavy distribution | 400V
315 | MCCB | C | 50, 70 | Large risers | 400V
400 | MCCB | C | 50, 70 | Main switchboards | 400V
630 | MCCB | Fixed | 50, 70 | Large switchboards | 400V
800 | ACB | Fixed | 65, 85 | Main incoming | 400V
1000 | ACB | Fixed | 65, 85 | Large incoming | 400V
1250 | ACB | Fixed | 85, 100 | Very large loads | 400V
1600 | ACB | Fixed | 85, 100 | Industrial mains | 400V
2000 | ACB | Fixed | 100 | Main busbars | 400V
Trip Curve Types:
B: 3-5 × In (sensitive circuits, long cables)
C: 5-10 × In (general use, most common)
D: 10-20 × In (motors, transformers, high inrush)
VOLTAGE DROP REQUIREMENTS (IEC 60364-5-52 / BS 7671)
Circuit Type | Max % Drop | From | Standard | Notes
Lighting Circuits | 3% | Origin | BS 7671 | More stringent for lighting
Power Circuits | 5% | Origin | BS 7671 | General use sockets/equipment
Motor Circuits | 5% | Origin | IEC 60364 | During starting conditions
Combined (Total) | 5% | Origin | IEC 60364 | Maximum total drop
Sub-distribution | 1-2% | Previous board | Engineering Practice | Allow headroom for final circuits
Temporary Supply | 6% | Origin | IEC 60364 | Construction sites only
Uganda-Specific Considerations:
• Grid voltage variation: ±10% (210-250V for 230V nominal)
• Consider voltage drop at minimum grid voltage
• Allow 2% margin for supply variations
• High ambient temperatures reduce cable capacity
CABLE TYPE SPECIFICATIONS
Cable Code | Full Name | Typical Sizes | Application | Voltage Rating | Standard
NYM | PVC Insulated Installation Cable | 1.5-10mm² | Fixed wiring in buildings | 300/500V | VDE 0250
NYAF | Flexible Stranded Conductor | 1.5-35mm² | Final connections, appliances | 450/750V | IEC 60227
NYY | PVC Insulated Power Cable | 16-400mm² | Distribution, underground | 0.6/1kV | VDE 0276
NYCY | Control/Signal Cable | 0.5-4mm² | Control circuits | 300/500V | IEC 60227
N2XY | XLPE Insulated Power Cable | 25-500mm² | HV distribution, underground | 6/10kV, 12/20kV | IEC 60502
H07RN-F | Rubber Cable Heavy Duty | 1.5-50mm² | Industrial, outdoor | 450/750V | IEC 60245
Armoured (SWA) | Steel Wire Armoured | 16-500mm² | Underground, exposed | 0.6/1kV | BS 5467
FP200 | Fire Resistant Cable | 1.5-25mm² | Fire alarm, emergency | 300/500V | BS 7629
Cat5e/Cat6 | Data Cable | 4-pair | Network/telecom | LV | TIA/EIA-568
UGANDA ELECTRICAL STANDARDS & REGULATIONS
Parameter | Value/Requirement | Authority | Notes
Nominal Voltage (Single Phase) | 230V ±10% | Umeme/ERA | Actual: 207-253V
Nominal Voltage (Three Phase) | 400V ±10% | Umeme/ERA | Actual: 360-440V
Frequency | 50Hz | ERA | Standard for East Africa
Power Factor Requirement | ≥0.85 | ERA | Industrial/commercial
Earthing System | TN-S or TN-C-S | IEC 60364 | TT in rural areas
Maximum Earth Loop Impedance | Per IEC 60364 | ERA | Depends on CB rating
RCD Protection | Required ≤32A sockets | BS 7671 | 30mA for personnel
Surge Protection | Recommended | IEC 62305 | Due to lightning risk
IP Rating (Outdoor) | IP54 minimum | IEC 60529 | Dust and moisture
Fire Rating | 60/90/120 min | Local Authority | Based on building type
Ambient Temperature | 30-40°C typical | Site conditions | Use in derating
Grid Stability | Variable | Umeme | UPS recommended for sensitive loads
Color Coding | Per IEC 60446 | ERA | Brown/Blue/Green-Yellow
Cable Standards | IEC 60227, IEC 60502 | UBS | Uganda Bureau of Standards
CB Standards | IEC 60898, IEC 60947 | UBS | Approved manufacturers only
Key Regulations:
• Electricity Act (Uganda)
• ERA (Electricity Regulatory Authority) Regulations
• Uganda National Bureau of Standards (UNBS)
• IEC and BS Standards (adopted)
• Local Authority Building Codes
ELECTRICAL CALCULATION FORMULAS
Calculation | Formula | Notes
Demand Load | Pd = Pc × DF | Pc=Connected load, DF=Diversity factor
Design Current (1P) | Ib = Pd / (V × PF) | V=Voltage, PF=Power factor
Design Current (3P) | Ib = Pd / (√3 × V × PF) | √3 = 1.732
CB Size Selection | In ≥ Ib | In=Nominal CB rating ≥ Design current
Cable Size Check | Iz ≥ In | Iz=Cable rating ≥ CB rating
Voltage Drop (1P) | Vd = (2 × L × Ib × ρ) / A | L=length(m), ρ=0.0175, A=CSA(mm²)
Voltage Drop (3P) | Vd = (√3 × L × Ib × ρ) / A | For balanced 3-phase loads
Voltage Drop % | Vd% = (Vd / Vn) × 100 | Vn=Nominal voltage
Earth Loop Impedance | Zs = Ze + (R1 + R2) | Ze=external, R1=phase, R2=earth
Fault Current | If = Uo / Zs | Uo=Phase-earth voltage
Disconnection Time | t = k²S² / I² | IEC 60364-4-41
Panel Total Load | ΣPd | Sum of all demand loads
Panel Utilization | U% = (Σ Ib / In,panel) × 100 | Should be <85%
Power (1P) | P = V × I × PF | Real power in watts
Power (3P) | P = √3 × V × I × PF | Three-phase power
Apparent Power | S = V × I | VA rating
Reactive Power | Q = √(S² - P²) | VAr (inductive)
Cable Resistance | R = ρ × L / A | Ohms, at 20°C
Correction Factor (Total) | Ct = Ca × Cg × Cd | Ambient × Grouping × Installation
Corrected Cable Rating | Iz,corrected = Iz × Ct | Apply all derating factors
UGANDA ELECTRICAL STANDARDS - EQUIPMENT & SYSTEMS
SECTION 1.1 - DISTRIBUTION PANELS per IEC 61439
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
DB | Distribution Board | General power distribution board per IEC 61439-2
EDB | Emergency Distribution Board | Emergency power distribution panel
ELDB | Emergency Lighting Distribution Board | Emergency lighting panel per IEC 60364-5-56
EMDB | Emergency Main Distribution Board | Emergency main switchboard
ESDB | Essential Services Distribution Board | Critical power distribution board
FDB | Floor Distribution Board | Floor-level sub-distribution panel
ISDB | Isolated Sub-Distribution Board | IT system isolated panel per IEC 60364-4-41
LDB | Local Distribution Board | Local area distribution panel
LSDB | Lighting Sub-Distribution Board | Lighting-specific sub-panel
MDB | Main Distribution Board | Building main distribution board
MLDB | Mechanical Lighting Distribution Board | MEP lighting distribution
MLVDB | Medium Low Voltage Distribution Board | MLV distribution panel
MMDB | Main-Main Distribution Board | Dual main distribution board
MSDB | Mechanical Sub-Distribution Board | HVAC power sub-panel
PSDB | Power Sub-Distribution Board | Power distribution sub-panel
SDB | Sub-Distribution Board | General sub-distribution board
SMDB | Sub-Main Distribution Board | Sub-main distribution panel
ZDB | Zone Distribution Board | Zone-specific distribution panel
SECTION 1.2 - SWITCHBOARDS & SWITCHGEAR per IEC 62271
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
ATS | Automatic Transfer Switch | Auto transfer switch per IEC 60947-6-1
BATS | Bypass Automatic Transfer Switch | Bypass ATS with maintenance bypass
EATS | Emergency Automatic Transfer Switch | Emergency power ATS
EMSB | Emergency Main Switchboard | Emergency MSB per IEC 60364
LVAC | LV Air Circuit Breaker Panel | Low voltage ACB panel per IEC 60947-2
LVMC | LV Moulded Case Panel | LV MCCB panel
LVMCC | LV Motor Control Center | Motor control center per IEC 61439-2
LVSG | Low Voltage Switchgear | LV switchgear <1kV per IEC 61439
MATS | Main Automatic Transfer Switch | Main service ATS
MMSB | Main-Main Switchboard | Dual main switchboard
MSB | Main Switchboard | Main electrical switchboard per IEC 61439-1
MVSG | Medium Voltage Switchgear | MV switchgear 1-36kV per IEC 62271-200
RMU | Ring Main Unit | MV ring main unit per IEC 62271-200
SATS | Sub Automatic Transfer Switch | Sub-panel ATS
SF6 | SF6 Gas Insulated Switchgear | SF6 GIS per IEC 62271-203
SMSB | Sub-Main Switchboard | Secondary switchboard
VCB | Vacuum Circuit Breaker Panel | VCB switchgear per IEC 62271-100
SECTION 1.3 - TRANSFORMERS per IEC 60076
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
AUTX | Auto Transformer | Autotransformer per IEC 60076-11
CTX | Control Transformer | Control circuit transformer
DTX | Dry Type Transformer | Dry-type distribution transformer per IEC 60076-11
FRTX | Furnace/Rectifier Transformer | Rectifier transformer for DC systems
ITX | Indoor Transformer | Indoor oil-filled transformer
KVTX | K-Rated Transformer | Harmonic-rated transformer (K-factor)
MEDTX | Medical Isolation Transformer | Medical IT transformer per IEC 61558-2-15
OTX | Oil Type Transformer | Oil-immersed transformer per IEC 60076
PTX | Pad Mounted Transformer | Outdoor pad-mount transformer
SOLTX | Solar Transformer | Solar inverter step-up transformer
STX | Step-Down Transformer | Voltage step-down transformer
SUTX | Step-Up Transformer | Voltage step-up transformer
TX | Transformer | General distribution transformer per IEC 60076
UVTX | Ultra Violet Transformer | UV lamp ballast transformer
SECTION 1.4 - GENERATORS & UPS per ISO 8528 / IEC 62040
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
BAT | Battery Bank | Battery energy storage system per IEC 61427
DFGEN | Dual Fuel Generator | Diesel/gas dual-fuel generator
DGEN | Diesel Generator | Diesel engine generator per ISO 8528
DUPS | Distributed UPS | Distributed/modular UPS architecture
EGEN | Emergency Generator | Emergency backup generator per NFPA 110
GEN | Generator Set | Engine-driven generator per ISO 8528-1
GGEN | Gas Generator | Natural gas engine generator
LIBAT | Lithium Battery | Lithium-ion battery system per IEC 62619
LIUPS | Line Interactive UPS | Line-interactive UPS topology per IEC 62040-3
MUPS | Modular UPS | Modular scalable UPS per IEC 62040-3
NIBAT | NiCd Battery | Nickel-cadmium battery per IEC 61951
OUPS | Online UPS | Double-conversion online UPS per IEC 62040-3
SGEN | Standby Generator | Standby power generator per ISO 8528-12
SUPS | Single UPS | Single-module UPS system
UPS | Uninterruptible Power Supply | UPS per IEC 62040 series
VBAT | VRLA Battery | Valve-regulated lead-acid battery per IEC 60896
SECTION 1.5 - CIRCUIT PROTECTION DEVICES per IEC 60947
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
ACB | Air Circuit Breaker | Air circuit breaker per IEC 60947-2
DISO | Distribution Isolator | Load break isolator switch
FISO | Fused Isolator | Fused disconnect switch per IEC 60947-3
ISO | Isolator | Isolation switch per IEC 60947-3
MCB | Miniature Circuit Breaker | MCB per IEC 60898-1
MCCB | Moulded Case Circuit Breaker | MCCB per IEC 60947-2
MISO | Main Isolator | Main service isolation switch
RCBO | Residual Current Breaker + O/L | RCD+overcurrent per IEC 61009
RCCB | Residual Current Circuit Breaker | RCD per IEC 61008
LAMP TECHNOLOGIES
Code | Specification | Description / Standard
LED | Light Emitting Diode | LED technology per IEC 62031, high efficiency
FL | Fluorescent | Fluorescent lamp technology
HAL | Halogen | Halogen incandescent
INC | Incandescent | Traditional incandescent
HID | High Intensity Discharge | HID lamp (metal halide, HPS)
HPS | High Pressure Sodium | HPS outdoor lighting
MH | Metal Halide | Metal halide HID
LPS | Low Pressure Sodium | LPS outdoor
CFL | Compact Fluorescent | CFL lamp
T5 | T5 Fluorescent | T5 linear fluorescent
T8 | T8 Fluorescent | T8 linear fluorescent
COLOR TEMPERATURES - Kelvin
Code | Specification | Description / Standard
2700 | 2700K | Warm white - residential
3000 | 3000K | Warm white - hospitality
3500 | 3500K | Neutral white
4000 | 4000K | Cool white - commercial
4500 | 4500K | Daylight white
5000 | 5000K | Daylight - retail
5500 | 5500K | Daylight
6000 | 6000K | Cool daylight - industrial
6500 | 6500K | Daylight - graphics/medical
CRI (Color Rendering Index) - CIE 13.3
Code | Specification | Description / Standard
70 | CRI 70 | Minimum for general lighting
75 | CRI 75 | Better color rendering
80 | CRI 80 | Good - commercial standard
85 | CRI 85 | Very good - retail
90 | CRI 90 | Excellent - art galleries
95 | CRI 95 | Superior - museums
97 | CRI 97 | Premium - medical/graphics
WIRE/CABLE SIZES - mm² (IEC 60228)
Code | Specification | Description / Standard
1.5 | 1.5mm² | Lighting circuits
2.5 | 2.5mm² | Power sockets
4 | 4mm² | Higher load circuits
6 | 6mm² | Cooker/water heater
10 | 10mm² | Sub-mains
16 | 16mm² | Distribution
25 | 25mm² | Main distribution
35 | 35mm² | Large loads
50 | 50mm² | Main feeders
70 | 70mm² | Heavy distribution
95 | 95mm² | Large feeders
120 | 120mm² | Main incoming
150 | 150mm² | Large capacity
185 | 185mm² | Heavy capacity
240 | 240mm² | Main distribution
300 | 300mm² | Large main
CIRCUIT BREAKER RATINGS - Amperes
Code | Specification | Description / Standard
6 | 6A | Small lighting circuits
10 | 10A | Lighting circuits
16 | 16A | Lighting/small power
20 | 20A | Power circuits
25 | 25A | Power circuits
32 | 32A | Cooker/heavy loads
40 | 40A | Large loads
50 | 50A | Sub-mains
63 | 63A | Distribution
80 | 80A | Distribution
100 | 100A | Main distribution
125 | 125A | Main panels
160 | 160A | Large distribution
200 | 200A | Heavy distribution
250 | 250A | Main incoming
400 | 400A | Large main
VOLTAGE CLASSIFICATIONS - IEC 60038
Code | Specification | Description / Standard
11000 | 11kV (MV) | Medium voltage 11,000V distribution
6600 | 6.6kV (MV) | Medium voltage 6,600V
3300 | 3.3kV (MV) | Medium voltage 3,300V
415 | 415V (LV) | Three-phase 415V per IEC 60038
400 | 400V (LV) | Three-phase 400V European standard
240 | 240V (LV) | Single-phase 240V
230 | 230V (LV) | Single-phase 230V IEC standard
220 | 220V (LV) | Single-phase 220V
110 | 110V (LV) | Reduced low voltage 110V
48 | 48V (ELV) | Extra low voltage 48V DC
24 | 24V (ELV) | Control voltage 24V DC/AC
12 | 12V (ELV) | Extra low voltage 12V
PHASE TYPES - IEC 60038
Code | Specification | Description / Standard
1PH | Single Phase | Single-phase AC power
3PH | Three Phase | Three-phase AC power per IEC 60038
DC | Direct Current | DC power supply
CIRCUIT LOAD TYPES
Code | Specification | Description / Standard
LTG | Lighting | Lighting circuits
PWR | Power | General power circuits
HVAC | HVAC | HVAC equipment circuits
EMG | Emergency | Emergency power circuits
ESS | Essential | Essential services circuits
IT | Information Technology | IT/data center circuits
KIT | Kitchen | Commercial kitchen circuits
MECH | Mechanical | Mechanical equipment power
MISC | Miscellaneous | General miscellaneous loads
MOUNTING TYPES
Code | Specification | Description / Standard
SM | Surface Mount | Surface-mounted installation
RC | Recessed | Recessed/flush installation
PD | Pendant | Suspended pendant mounting
WM | Wall Mount | Wall-mounted installation
CM | Ceiling Mount | Ceiling-mounted installation
FM | Floor Mount | Floor-standing installation
RM | Roof Mount | Roof-mounted installation
PM | Pole Mount | Pole-mounted installation
TM | Track Mount | Track-mounted system
BL | Bollard | Bollard-type installation
SP | Suspended | Suspended from structure
CC | Concealed | Concealed installation
EX | Exposed | Exposed installation
CS | Cassette | Cassette-type installation
DC | Ducted | Ducted concealed system
CABLE INSTALLATION METHODS - IEC 60364-5-52
Code | Specification | Description / Standard
Conduit | Conduit | Installed in conduit per IEC 60364-5-52
Tray | Cable Tray | On cable tray system
Trunking | Cable Trunking | In cable trunking
Ladder | Cable Ladder | On cable ladder
Buried | Direct Buried | Direct buried underground
Underground | Underground | Underground installation
Overhead | Overhead | Overhead installation
Clipped Direct | Clipped Direct | Clipped directly to surface
IP RATINGS - IEC 60529 (Ingress Protection)
Rating | Protection Level | Typical Applications
IP20 | Protected against solid objects >12.5mm | Indoor switchboards, general indoor use
IP21 | IP20 + dripping water (vertical) | Indoor equipment in damp locations
IP22 | IP20 + dripping water (15° tilt) | Indoor with condensation risk
IP40 | Protected against solid objects >1mm | Indoor equipment rooms
IP44 | IP40 + splashing water | Outdoor/indoor damp locations
IP54 | Dust protected + splashing water | Industrial, some dust exposure
IP55 | Dust protected + water jets | Industrial wash-down areas
IP65 | Dust tight + water jets | Outdoor equipment, complete dust protection
IP66 | Dust tight + powerful water jets | Marine, heavy wash-down
IP67 | Dust tight + temporary immersion | Submersible equipment (temporary)
IP68 | Dust tight + continuous immersion | Permanent submersion applications
ADDITIONAL TECHNICAL DATA
Classification | Voltage Range | Typical Applications
ELV | Extra Low Voltage: ≤50V AC / ≤120V DC | Control systems, telecommunications, BMS
LV | Low Voltage: 50-1000V AC / 120-1500V DC | Building distribution, 230V/400V/480V systems
MV | Medium Voltage: 1kV-35kV | Campus distribution, large facilities, substations
HV | High Voltage: >35kV | Utility transmission, not typical in buildings
UGANDA ELECTRICAL STANDARDS - TECHNICAL CODES & SPECIFICATIONS
STANDARD CURRENT RATINGS (IEC 60269)
Rating (A) | Application | Fuse Type | Circuit Type | Breaking Capacity | Standard
1 | Control circuits | gG | Signal/Control | 50kA | IEC 60269-2
2 | Small control | gG | Control | 50kA | IEC 60269-2
3 | Lighting circuits | gG | Lighting | 50kA | IEC 60269-2
5 | Small appliances | gG | Power | 50kA | IEC 60269-2
6 | Lighting/small power | gG | Mixed | 50kA | IEC 60269-2
10 | General power | gG | Power | 50kA | IEC 60269-2
13 | UK ring main | gG | Ring circuit | 50kA | BS 1362
15 | Power circuits | gG | Power | 50kA | IEC 60269-2
16 | Standard sockets | gG | Power | 50kA | IEC 60269-2
20 | Heavy appliances | gG | Power | 80kA | IEC 60269-2
25 | Sub-circuits | gG | Distribution | 80kA | IEC 60269-2
32 | Large loads | gG | Distribution | 80kA | IEC 60269-2
40 | Sub-mains | gG | Distribution | 100kA | IEC 60269-2
50 | Distribution | gG | Sub-main | 100kA | IEC 60269-2
63 | Large distribution | gG | Main | 100kA | IEC 60269-2
80 | Main feeders | gG | Main | 120kA | IEC 60269-2
90 | Main incoming | gG | Incoming | 120kA | IEC 60269-2
CONDUIT SIZES (IEC 61386)
Conduit Size (mm) | Internal Diameter | Max Cable Fill | Typical Cable Capacity | Application | Material
16mm | 13mm | 40% | 2×2.5mm² or 3×1.5mm² | Small installations | PVC/Steel
20mm | 16mm | 40% | 3×2.5mm² or 4×1.5mm² | Lighting circuits | PVC/Steel
25mm | 21mm | 40% | 4×2.5mm² or 6×1.5mm² | Power circuits | PVC/Steel
32mm | 28mm | 40% | 6×2.5mm² or 3×4mm² | Standard distribution | PVC/Steel
40mm | 35mm | 40% | 8×2.5mm² or 4×6mm² | Heavy circuits | PVC/Steel
50mm | 44mm | 40% | 12×2.5mm² or 6×6mm² | Sub-mains | PVC/Steel
63mm | 56mm | 40% | 16×2.5mm² or 8×6mm² | Large distribution | PVC/Steel
75mm | 67mm | 40% | 3×16mm² or 20×2.5mm² | Main feeders | PVC/Steel
90mm | 81mm | 40% | 4×25mm² or 3×35mm² | Main distribution | PVC/Steel
100mm | 90mm | 40% | 4×35mm² or 3×50mm² | Main incoming | PVC/Steel
CABLE CORES & CONFIGURATIONS (IEC 60228)
Core Code | Description | Typical Use | Phase Config | Color Code | Standard
1C | Single core cable | Phase/Neutral/Earth | Single conductor | Brown/Blue/G-Y | IEC 60446
2C | Two core cable | 1-phase with neutral | L+N | Brown, Blue | IEC 60446
3C | Three core cable | 1-phase + earth or 3-phase | L,N,E or 3L | Brown,Blue,G-Y or Brown,Black,Grey | IEC 60446
4C | Four core cable | 3-phase with neutral | 3L+N | Brown,Black,Grey,Blue | IEC 60446
5C | Five core cable | 3-phase with N+E | 3L+N+E | Brown,Black,Grey,Blue,G-Y | IEC 60446
3C+E | Three core plus earth | 3-phase with separate earth | 3L+E | Brown,Black,Grey + G-Y | IEC 60446
4C+E | Four core plus earth | 3-phase with N+E | 3L+N+E | Brown,Black,Grey,Blue + G-Y | IEC 60446
7C | Seven core cable | Control/instrumentation | Multi-signal | Various | IEC 60227
12C | Twelve core cable | Complex control | Multi-signal | Numbered | IEC 60227
19C | Nineteen core cable | Instrumentation | Multi-signal | Numbered | IEC 60227
SWITCH TYPES & CONFIGURATIONS
Switch Code | Description | Gang Configuration | Typical Rating | Application | Standard
1G-SW | Single gang switch | 1 gang | 10A/16A | Single circuit control | IEC 60669-1
2G-SW | Double gang switch | 2 gang | 10A/16A | Two circuit control | IEC 60669-1
3G-SW | Triple gang switch | 3 gang | 10A/16A | Three circuit control | IEC 60669-1
4G-SW | Four gang switch | 4 gang | 10A/16A | Four circuit control | IEC 60669-1
ISO-SW | Isolation switch | N/A | 20A-63A | Circuit isolation | IEC 60947-3
DIM-SW | Dimmer switch | 1-4 gang | 200W-1000W | Light dimming | IEC 60669-2-1
TIM-SW | Timer switch | 1 gang | 16A | Time-based control | IEC 60730
PIR-SW | Motion sensor switch | 1 gang | 10A | Occupancy detection | IEC 60669-2-3
2W-SW | Two-way switch | 1-4 gang | 10A/16A | Multi-point control | IEC 60669-1
INT-SW | Intermediate switch | 1-4 gang | 10A/16A | 3+ point control | IEC 60669-1
PULL-SW | Pull cord switch | 1 gang | 6A | Bathroom lighting | IEC 60669-1
KEY-SW | Key switch | 1 gang | 10A | Secure control | IEC 60669-1
POLE CONFIGURATIONS (IEC 60947)
Pole Config | Description | Phase Coverage | Application | Typical Voltage | Standard
1P | Single pole | Phase only | AC single phase (phase switching) | 230V | IEC 60947-2
2P | Double pole / 2-pole | Phase + Neutral | AC single phase (full isolation) | 230V | IEC 60947-2
3P | Three pole / 3-pole | Three phases | AC three phase (no neutral) | 400V | IEC 60947-2
3P+N | Three pole plus neutral | Three phases + Neutral | AC three phase with switched neutral | 400V | IEC 60947-2
4P | Four pole | Three phases + Neutral | AC three phase (full isolation) | 400V | IEC 60947-2
1P+N | Single pole plus neutral | Phase + Neutral | Single phase with neutral switching | 230V | IEC 60947-2
UGANDA ELECTRICAL STANDARDS - FIXTURES, DEVICES & MATERIALS
ELECTRICAL FIXTURE TYPES (IEC 60598)
Fixture Code | Fixture Type | Description | Mounting | IP Rating | Application | Standard
REC | Recessed Fixture | Ceiling recessed downlight | Recessed | IP20-IP44 | Indoor ceilings | IEC 60598-2-2
SUR | Surface Fixture | Surface mounted luminaire | Surface | IP20-IP65 | Walls/ceilings | IEC 60598-1
PEN | Pendant Fixture | Suspended pendant light | Suspended | IP20-IP44 | Indoor spaces | IEC 60598-1
TRK | Track Fixture | Track-mounted spotlight | Track | IP20 | Retail/display | IEC 60598-2-2
WAL | Wall Fixture | Wall-mounted luminaire | Wall | IP44-IP65 | Indoor/outdoor walls | IEC 60598-1
FLR | Floor Fixture | Floor-standing lamp | Floor | IP20 | Indoor spaces | IEC 60598-1
UDR | Under-cabinet Fixture | Under-cabinet light | Under-mount | IP20 | Kitchens | IEC 60598-1
EXT | Exterior Fixture | Outdoor luminaire | Wall/pole | IP65-IP67 | Outdoor | IEC 60598-2-3
EMG | Emergency Fixture | Emergency lighting | Various | IP20-IP65 | Exit/emergency | IEC 60598-2-22
IND | Industrial Fixture | High-bay/low-bay | Suspended/chain | IP65 | Warehouses/factories | IEC 60598-2-5
STR | Street Fixture | Street light/post-top | Pole-mount | IP66 | Roads/parking | IEC 60598-2-3
FLD | Floodlight Fixture | Wide-area floodlight | Ground/wall | IP65-IP67 | Sports/security | IEC 60598-2-5
ELECTRICAL DEVICE TYPES (IEC 60884 / IEC 60669)
Device Code | Device Type | Description | Rating | Configuration | Application | Standard
SKT | Socket Outlet | Power socket outlet | 13A/16A | 1-gang to 4-gang | General power | IEC 60884-1
SKT-USB | Socket with USB | Socket with USB charging | 13A+USB | 1-2 gang + USB | Device charging | IEC 60884-1
SKT-RCD | RCD Socket | Socket with RCD protection | 13A/16A | With 30mA RCD | Wet areas | IEC 61008
SKT-IP | Weatherproof Socket | IP-rated outdoor socket | 16A | IP44-IP66 | Outdoor use | IEC 60884-1
SW-1G | 1-Gang Switch | Single switch | 10A/16A | 1-way/2-way | Lighting control | IEC 60669-1
SW-2G | 2-Gang Switch | Double switch | 10A/16A | 1-way/2-way | Multi-circuit | IEC 60669-1
SW-DIM | Dimmer Switch | Light dimmer control | 200W-1kW | Rotary/push | Lighting dimming | IEC 60669-2-1
SW-PIR | PIR Switch | Motion sensor switch | 10A | Automatic | Occupancy control | IEC 60669-2-3
SW-TIM | Timer Switch | Time delay switch | 16A | Programmable | Timed control | IEC 60730
TERM | Terminal Block | Connection terminal | Varies | 2-12 pole | Cable termination | IEC 60947-7-1
ISO | Isolator | Load isolator | 20A-100A | Rotary/toggle | Circuit isolation | IEC 60947-3
FCU | Fused Connection Unit | Fused spur | 13A | With fuse | Fixed appliances | BS 1363
CCU | Clock Connector | Clock/timer connector | 3A | Unswitched | Clock circuits | IEC 60884
SHAV | Shaver Socket | Bathroom shaver socket | 1A | Isolated transformer | Shavers/toothbrushes | IEC 61558-2-5
TEL | Telephone Socket | Telephone outlet | N/A | RJ11 | Landline phones | IEC 60603-7
DATA | Data Socket | Network data outlet | N/A | RJ45 Cat5e/6 | Data networks | IEC 60603-7
TV | TV/Satellite Socket | Coaxial TV outlet | N/A | Coaxial | TV/satellite | IEC 61169-2
BELL | Bell Push | Doorbell button | 1A | Momentary | Doorbells | IEC 60669-1
LIGHTING DEVICE TYPES (IEC 60929 / IEC 62386)
Device Code | Device Type | Description | Power Range | Control Type | Application | Standard
DRV-LED | LED Driver | Constant current/voltage driver | 10W-300W | Non-dimmable/Dimmable | LED lighting | IEC 61347-2-13
BAL-FL | Fluorescent Ballast | Electronic/magnetic ballast | 18W-58W | Instant start | Fluorescent tubes | IEC 60929
BAL-CFL | CFL Ballast | Integrated ballast | 9W-32W | Integrated | CFL lamps | IEC 60929
BAL-HID | HID Ballast | High intensity discharge ballast | 35W-400W | Electronic/magnetic | HID lamps | IEC 61167
TRF-HAL | Halogen Transformer | Electronic/toroidal transformer | 20W-300W | Low voltage | Halogen 12V | IEC 61558-2-6
DIM-TRAIL | Trailing Edge Dimmer | TRIAC dimmer | 60W-400W | Phase control | Incandescent/halogen | IEC 60669-2-1
DIM-LEAD | Leading Edge Dimmer | Forward phase dimmer | 100W-1000W | Phase control | Resistive loads | IEC 60669-2-1
DIM-LED | LED Dimmer | PWM/0-10V dimmer | 10W-200W | PWM/analog | LED dimmable | IEC 60669-2-1
DIM-FL | Fluorescent Dimmer | Ballast dimmer | 18W-216W | DSI/DALI | Dimmable fluorescent | IEC 62386
CTRL-DALI | DALI Controller | Digital addressable control | N/A | DALI protocol | Smart lighting | IEC 62386
CTRL-DMX | DMX Controller | DMX512 lighting controller | N/A | DMX protocol | Stage/architectural | ANSI E1.11
SENS-PIR | PIR Sensor | Passive infrared motion sensor | 10A | Motion detection | Occupancy lighting | IEC 60669-2-3
SENS-LUX | Daylight Sensor | Photocell/lux sensor | 10A | Light level | Daylight harvesting | IEC 60669-2-3
EMER-INV | Emergency Inverter | Battery backup inverter | 3W-80W | Auto-switching | Emergency lighting | IEC 61347-2-7
EMER-BAT | Emergency Battery Pack | Self-contained battery | 3-8 hours | Auto-test | Emergency fixtures | IEC 60598-2-22
ELECTRICAL MATERIAL CODES
Material Code | Material Name | Description | Properties | Temperature Rating | Application | Standard
PVC | Polyvinyl Chloride | Thermoplastic insulation | Rigid/flexible, flame retardant | 70°C-105°C | Cable insulation, conduit | IEC 60227
XLPE | Cross-linked Polyethylene | Thermoset insulation | High temperature, moisture resistant | 90°C-120°C | Power cables | IEC 60502
EPR | Ethylene Propylene Rubber | Synthetic rubber insulation | Flexible, heat resistant | 90°C | Flexible cables | IEC 60245
SILICONE | Silicone Rubber | High-temp rubber | Very flexible, high temperature | 180°C-200°C | High-temp cables | IEC 60245
CU | Copper | Conductor material | High conductivity (58 MS/m) | N/A | Cable conductors | IEC 60228
AL | Aluminum | Conductor material | Lower conductivity (37 MS/m) | N/A | Large cables | IEC 60228
STEEL | Steel | Armor/protection | Mechanical protection | N/A | Cable armor, conduit | BS 5467
GALV | Galvanized Steel | Zinc-coated steel | Corrosion resistant | N/A | Conduit, trunking | IEC 61386
SS | Stainless Steel | Corrosion-resistant steel | High corrosion resistance | N/A | Harsh environments | IEC 61386
BRASS | Brass | Copper-zinc alloy | Corrosion resistant | N/A | Cable glands, terminals | Various
PC | Polycarbonate | Engineering thermoplastic | High impact, transparent | 120°C | Switch plates, enclosures | IEC 60695
ABS | ABS Plastic | Thermoplastic polymer | Impact resistant | 80°C | Enclosures, boxes | IEC 60695
NYLON | Nylon/Polyamide | Engineering plastic | Strong, abrasion resistant | 85°C-150°C | Cable ties, glands | Various
GRP | Glass Reinforced Plastic | Fiberglass composite | High strength, non-conductive | 120°C | Cable trays, enclosures | IEC 61537
FLOOR LEVELS
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
B03 | Basement 3 | Third basement level
B02 | Basement 2 | Second basement
B01 | Basement 1 | First basement
LG | Lower Ground | Semi-basement
L00 | Ground Floor | Main entrance
LM | Mezzanine | Intermediate level
L01 | Level 1 | First floor
L02 | Level 2 | Second floor
L03 | Level 3 | Third floor
L04 | Level 4 | Fourth floor
L05 | Level 5 | Fifth floor
L06 | Level 6 | Sixth floor
L07 | Level 7 | Seventh floor
LP | Penthouse | Upper level
LR | Roof | Roof level
ZONE CODES
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
Z01 | Zone 1 | Primary zone
Z02 | Zone 2 | Secondary zone
Z03 | Zone 3 | Tertiary zone
Z04 | Zone 4 | Fourth zone
Z05 | Zone 5 | Fifth zone
COR | Corridor | Circulation areas
EXT | External | Outdoor equipment
PKG | Parking | Parking garage
PLANT | Plant Room | MEP plant room
ROOF | Roof | Roof equipment
SVC | Service | Service areas
UTIL | Utility | Utility rooms
DISCIPLINE CODES - ISO 19650-2
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
C | Controls/BMS | ISO 16484
D | Data/Telecom | ISO/IEC 11801
E | Electrical | IEC 60364
F | Fire Protection | NFPA 13
FA | Fire Alarm | NFPA 72
KIT | Kitchen | NFPA 96
L | Lighting | IEC 60598
LAB | Laboratory | Lab systems
LAU | Laundry | Laundry equipment
M | Mechanical | ASHRAE
MG | Medical Gas | ISO 7396
P | Plumbing | ISO 15874
RE | Renewable | Solar/wind
S | Security | Access/CCTV
VT | Vertical Transport | Elevators
CURRENT_RATINGS | CURRENT_RATINGS_DESCRIPTION
1
2
3
5
6
10
13
15
16
20
25
30
32
40
45
50
60
63
75