## ISO 16484-MECHANICAL
ISO 16484 - MECHANICAL, VENTILATION AND AIR CONDITIONING SYSTEMS |  |  |  | Section 3.2 - CONDENSING UNITS & CHILLERS per ASHRAE Standards |  |  |  | Section 3.3 - SPLIT & PACKAGED AC UNITS per ISO 5151 |  |  | Section 3.4 - FAN COIL UNITS (FCU) |  |  | Section 3.5 - FANS & BLOWERS per AMCA 200/210 |  |  | Section 3.6 - DIFFUSERS & GRILLES per ASHRAE Fundamentals |  |  | Section 3.7 - DAMPERS & ACTUATORS per UL 555/555S |  |  | Section 3.8 - VAV & CAV TERMINAL UNITS per AHRI 880 |  |  | Section 3.9 - BOILERS & HEATERS per ASME Section IV |  |  | Section 3.10 - PUMPS per ASME B73.1/HI Standards |  |  | REFRIGERANTS - ISO 817 / ASHRAE 34 |  |  | MEDICAL GAS OUTLETS - ISO 7396-1 |  |  | DUCT TYPES |  |  | TERMINAL TYPES |  |  | DUCT MATERIALS |  |  | INSULATION |  |  | TERMINAL TYPES (DETAILED) |  |  | MOUNTING TYPES |  |  | CONTROLS |  | MOUNTING
Uganda Standards 2025 - Enhanced Version |  |  |  | Code | Description | Technical Specification / Standard Reference |  | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Specification | Description / Standard | Code | Description | Standard / Specification | Code | Description | Standard / Specification | Code | Description | Standard / Specification | Code | Description | Standard / Specification | Code | Thickness / Type | Application | Code | Description | Standard / Specification | Code | Description | Standard / Specification | Code | Description | Code | Description
Section 3.1 - AIR HANDLING UNITS (AHU) per ISO 16484-3 |  |  |  | ABCH | Absorption Chiller | Heat-driven absorption cycle chiller (LiBr/H2O or NH3/H2O) |  | AC | Air Conditioner | General air conditioning unit | CFCU | Concealed Fan Coil Unit | Ceiling-concealed FCU with ducted supply/return | AEF | Axial Exhaust Fan | Axial flow exhaust fan per AMCA 210 | CREG | Ceiling Register | Adjustable ceiling supply register | BD | Backdraft Damper | Gravity-operated backdraft prevention damper | CAV | Constant Air Volume Box | CAV terminal unit with fixed airflow | BLR | Boiler | Hot water/steam boiler per ASME Section IV | PUMP-CHW | Chilled Water Pump | Chilled water circulation pump per HI 1.3 | R-410A | R-410A (HFC) | Common residential/commercial, GWP 2088, per ASHRAE 34 | AIRMAN | Air Manifold | Medical air manifold | SD | Supply Duct | Fibreglass duct board ASTM C1071 | SD-SQ | Square Supply Diffuser | ASHRAE 70-2006 | GI | Galvanized Iron | ASTM A653 | SD | Fibreglass 25mm | Supply Duct | SD-SQ | Square Supply Diffuser |  | GI | Floor | Galvanized iron per ASTM A653 | DDC Control | Direct digital control per ISO 16484 | Floor Mount | Floor mounting per equipment specs
AHU_CODE | AHU_CODE_DESCRIPTION | Technical Specification / Standard Reference |  | ACDU | Air Cooled Condensing Unit | Air-cooled refrigerant condensing unit per AHRI 365 |  | CPAC | Close Control Package AC | Precision AC for data centers per ASHRAE TC 9.9 | CSFCU | Cassette Fan Coil Unit | Ceiling cassette FCU with 4-way distribution | ASF | Axial Supply Fan | Axial flow supply fan | CRG | Ceiling Return Grille | Fixed ceiling return air grille | BDACT | Belimo Damper Actuator | Belimo brand damper actuator (common spec) | DDVAV | Dual Duct VAV Box | Dual duct mixing VAV terminal | CBLR | Condensing Boiler | High-efficiency condensing boiler >90% AFUE | PUMP-CDW | Condenser Water Pump | Condenser/tower water pump | R-32 | R-32 (HFC) | Lower GWP alternative, GWP 675, increasingly used | AIROUT | Medical Air Outlet | Air terminal unit | RG | Return Grille | SMACNA HVAC Duct Construction Standards | SD-RD | Round Supply Diffuser | ASHRAE 70-2006 | STAINLESS | Stainless Steel | ASTM A240 | RG | Fibreglass 50mm | Return Duct / Return Grille | SD-RD | Round Supply Diffuser |  | STAINLESS | Wall | Stainless steel 304/316 per ASTM A240 | ON/OFF Control | Two-position on/off control | Wall Mount | Wall mounting per equipment specs
HAHU | Hygienic Air Handling Unit | Cleanroom AHU with HEPA filtration per ISO 14644 |  | ACH | Air Cooled Chiller | Air-cooled chiller per AHRI 550/590 |  | CSP | Ceiling Split Unit | 4-way cassette ceiling split system | EFCU | Exposed Fan Coil Unit | Wall/ceiling exposed FCU | ATRF | Atrium Relief Fan | Smoke relief fan for atrium spaces | CSD | Circular Supply Diffuser | Round ceiling supply diffuser | DACT | Damper Actuator | Motorized damper actuator per ISO 16484 | FVAV | Fan Powered VAV Box | VAV with integral supply fan | CHTR | Convection Heater | Natural convection space heater | PUMP-HW | Heating Water Pump | Hot water heating circulation pump | R-134a | R-134A (HFC) | Chillers/automotive, GWP 1430 | CO2OUT | CO2 Outlet | Carbon dioxide outlet | EG | Exhaust Grille | SMACNA HVAC Duct Construction Standards | RG-SL | Slot Return Grille | ASHRAE 70-2006 | ALUMINUM | Aluminum | ASTM B209 | EG | Armaflex 13mm | Exhaust Duct / Extract Grille | RG-SL | Return Grille - Slot |  | ALUMINUM | Ceiling | Aluminum per ASTM B209 | VFD Control | Variable frequency drive control | Ceiling Mount | Ceiling mounting per equipment specs
LAHU | Laboratory Air Handling Unit | Lab-specific AHU with enhanced safety and exhaust |  | CCCT | Closed Circuit Cooling Tower | Closed-circuit fluid cooler per CTI STD-201 |  | DSP | Duct Split Unit | Concealed ceiling ducted split system | FCDU | Fan Coil Duct Unit | Ducted fan coil unit | BLW | Blower | General centrifugal blower | DBG | Double Deflection Grille | Adjustable double deflection supply grille | EDACT | Electric Damper Actuator | Electric motor damper actuator | PVAV | Parallel Fan VAV Box | Parallel fan-powered VAV per AHRI 880 | EBLR | Electric Boiler | Electric resistance boiler |  |  |  | R-407C | R-407C (HFC) | R-22 retrofit, GWP 1774 | N2OMAN | N2O Manifold | Nitrous oxide manifold | VAV | VAV Terminal | AHRI 880 | RG-DW | Double Deflection Return/Extract Grille | ASHRAE 70-2006 | FLEXIBLE | Flexible Duct | UL 181 | OA | Armaflex 19mm | Outside Air Duct | RG-EG | Return/Extract Grille |  | FRP | Roof | Fiberglass reinforced plastic per ASTM D4097 | Thermostat | Room thermostat per ISO 7730 | Roof Mount | Roof mounting per equipment specs
MAHU | Modular Air Handling Unit | Flexible modular construction AHU system |  | CDU | Condensing Unit | General refrigerant condensing unit per AHRI 365 |  | FSP | Floor Split Unit | Floor console type split indoor unit | FCU | Fan Coil Unit | Standard chilled/hot water fan coil per ISO 16358-1 | BPRF | Building Pressurization Fan | Stairwell pressurization per NFPA 92 | DRG | Door Return Grille | Door-mounted return air transfer grille | FD | Fire Damper | Fusible link fire damper per UL 555 | SCAV | Single Duct CAV Box | Single duct CAV terminal | EWH | Electric Water Heater | Electric domestic hot water heater |  |  |  | R-404A | R-404A (HFC) | Commercial refrigeration, GWP 3922 | N2OUT | N2O Outlet | Nitrous oxide outlet | CAV | CAV Terminal | AHRI 880 | EG-SL | Slot Exhaust Grille | ASHRAE 70-2006 | FIBREGLASS | Fibreglass | ASTM C1071 | SA | Armaflex 25mm | Supply Air (general) | SD-4W | 4-Way Supply Diffuser |  | PVC | Suspended | PVC duct per ASTM D1784 | Humidistat | Humidity control per ISO 16484-2 | Suspended | Suspended mounting per equipment specs
MAU | Make-Up Air Unit | Replacement air unit compensating for exhaust systems |  | CH | Chiller | General chiller per ASHRAE 90.1 |  | MSAC | Multi-Split AC | Multi-zone split with multiple indoor units | HFCU | Horizontal Fan Coil Unit | Horizontal concealed FCU | CEF | Centrifugal Exhaust Fan | Centrifugal exhaust fan | EGG | Egg Crate Grille | Egg crate pattern return grille | FSD | Fire/Smoke Damper | Combination fire and smoke damper per UL 555S | SCVAV | Single Duct CAV Box | Single duct VAV terminal unit | FSHTR | Fan Space Heater | Unit heater with integral fan |  |  |  | R-22 | R-22 (HCFC) | PHASED OUT per Montreal Protocol - legacy only | O2MAN | Oxygen Manifold | Oxygen cylinder manifold | DIFF | Supply Diffuser | ASHRAE 70-2006 | DIFF-SQ | Square Diffuser | ASHRAE 70-2006 | PVC | PVC | ASTM D1784 | RA | PIR 25mm | Return Air | SD-LN | Linear Supply Diffuser |  | FLEX | Ducted | Flexible duct per UL 181 | CO2 Sensor | Demand control ventilation per ASHRAE 62.1 | Ducted | Ducted installation
PAHU | Package Air Handling Unit | Factory-assembled pre-wired packaged AHU |  | CT | Cooling Tower | Cooling tower per CTI ATC-105 |  | PAC | Package Air Conditioner | Self-contained packaged AC unit | HWFCU | Hot Water Fan Coil Unit | Heating-only hot water FCU | CORPF | Corridor Pressurization Fan | Corridor smoke control fan | FREG | Floor Register | Floor-mounted supply register | MCD | Motorized Control Damper | Modulating control damper with actuator | SVAV | Series Fan VAV Box | Series fan-powered VAV per AHRI 880 | GBLR | Gas Boiler | Natural gas fired boiler |  |  |  | WATER | Water | Water as refrigerant/coolant | O2OUT | Oxygen Outlet | Oxygen terminal unit | GRILLE | Return Grille | ASHRAE 70-2006 | DIFF-RD | Round Diffuser | ASHRAE 70-2006 |  | PVC | ASTM D1784 | EA | Mineral wool 50mm | Exhaust Air | SD-SW | Swirl Diffuser |  | FABRIC | Cassette | Fabric ducting system | Timer | Programmable timer control | Cassette | Ceiling cassette installation
RAHU | Rooftop Air Handling Unit | Weatherproof outdoor rooftop-mounted AHU |  | CENCH | Centrifugal Chiller | Centrifugal compressor chiller per AHRI 550/590 |  | PPAC | Portable Package AC | Mobile packaged unit on casters | SLFCU | Slim Line Fan Coil Unit | Ultra-thin profile FCU | CSF | Centrifugal Supply Fan | Centrifugal supply air fan | FRG | Floor Return Grille | Floor-mounted return grille | MVD | Manual Volume Damper | Manual balancing volume damper | TCAV | Throttling CAV Box | CAV with throttling damper | GWH | Gas Water Heater | Gas-fired water heater per ANSI Z21.10.1 |  |  |  | STEAM | Steam | Steam heating medium | VAOUT | Vacuum Outlet | Medical vacuum outlet | DAMPER | Damper | SMACNA damper standards | [6 empty] | FA | Elastomeric foam 19mm | Fresh Air | EG-LV | Louvre Extract Grille |  |  | Floor Mount |  | BMS Integration | Building management system integration
VMAU | Ventilation Make-Up Air Unit | Tempered outdoor air ventilation unit |  | FDCT | Forced Draft Cooling Tower | Tower with bottom-mounted fan forcing air upward |  | RPAC | Rooftop Package AC | Rooftop unit (RTU) per AHRI 340/360 | VFCU | Vertical Fan Coil Unit | Vertical stack/riser FCU | EF | Exhaust Fan | General exhaust ventilation fan | LINRG | Linear Return Grille | Slot-type linear return grille | PDACT | Pneumatic Damper Actuator | Compressed air damper actuator | VAV | Variable Air Volume Box | VAV terminal unit with DDC control per ASHRAE | HPWH | Heat Pump Water Heater | Heat pump domestic hot water system |  |  |  | GLYCOL | Glycol Solution | Water-glycol antifreeze solution | WAGD | WAGD System | Waste gas disposal | FD | Fire Damper | UL 555 | [9 empty] | DDC
|  |  |  | HCT | Hybrid Cooling Tower | Wet/dry hybrid cooling system for water conservation |  | VRF | Variable Refrigerant Flow | VRF system per ISO 16358 |  |  |  | HXFAN | Heat Recovery Fan | Energy recovery ventilator fan | LSD | Linear Supply Diffuser | Slot diffuser for perimeter heating | RD | Relief Damper | Barometric/motorized relief damper |  |  |  | NCBLR | Non-Condensing Boiler | Standard efficiency non-condensing boiler | [9 empty] | MD | [11 empty] | ON/OFF
|  |  |  | ICT | Induced Draft Cooling Tower | Tower with top-mounted fan inducing air through fill |  | VRV | Variable Refrigerant Volume | Daikin VRV trademark system |  |  |  | JET | Jet Fan | Impulse jet fan for tunnels/parking per BS EN 12101-3 | PERF | Perforated Diffuser | Perforated ceiling diffuser panel | VD | Volume Damper | Airflow balancing damper per SMACNA |  |  |  | OBLR | Oil Boiler | Oil-fired boiler | [21 empty] | VFD
|  |  |  | MCH | Modular Chiller | Modular design chiller for staged capacity |  | WSP | Wall Split Unit | Wall-mounted split indoor unit |  |  |  | KEF | Kitchen Exhaust Fan | Commercial kitchen exhaust per NFPA 96 | PERRG | Perforated Return Grille | Perforated return grille | [6 empty] | RHTR | Radiant Heater | Radiant tube/panel heater | [21 empty] | THERMOSTAT
|  |  |  | OCT | Open Cooling Tower | Traditional open-circuit evaporative tower | [7 empty] | LABEF | Laboratory Exhaust Fan | Fume hood exhaust fan | REG | Register | General adjustable register | [6 empty] | SHTR | Space Heater | General space heating unit | [21 empty] | HUMIDISTAT
|  |  |  | RCDU | Rack Condensing Unit | Multi-compressor rack for refrigeration | [7 empty] | MIXFAN | Mixing Fan | Air circulation mixing fan | RG | Return Grille | Fixed blade return grille per ASHRAE | [6 empty] | SWH | Solar Water Heater | Solar thermal water heating system | [21 empty] | CO2
|  |  |  | SCH | Screw Chiller | Twin-screw compressor chiller technology | [7 empty] | PSF | Plenum Supply Fan | Plenum mounted supply fan | SD | Supply Diffuser | Ceiling supply air diffuser | [6 empty] | UHTR | Unit Heater | Suspended gas/electric unit heater | [21 empty] | TIMER
|  |  |  | WCDU | Water Cooled Condensing Unit | Water-cooled refrigerant condenser | [7 empty] | SEF | Smoke Exhaust Fan | Smoke extraction fan per BS EN 12101-3 | SSD | Square Supply Diffuser | Square ceiling diffuser | [6 empty] | WH | Water Heater | Domestic hot water heater per ASHRAE 90.1 | [21 empty] | BMS
|  |  |  | WCH | Water Cooled Chiller | Water-cooled chiller with cooling tower circuit | [7 empty] | SF | Supply Fan | General supply air fan | SWD | Swirl Diffuser | Swirl pattern supply diffuser
[14 empty] | STPF | Staircase Pressurization Fan | Fire stair pressurization per IBC | TRFG | Transfer Grille | Door/wall transfer grille
[14 empty] | TOILEF | Toilet Exhaust Fan | Restroom exhaust ventilation fan | WREG | Wall Register | Wall-mounted supply register
[17 empty] | WRG | Wall Return Grille | Wall-mounted return grille
COMPREHENSIVE HVAC FORMULAS - ASHRAE / ISO 16484
Formula Category | Formula Name | Formula | Variables | Units | Notes |  | DUCT SIZING CALCULATOR
Air Flow | Volume Flow Rate | Q = v × A | Q=Flow rate, v=Velocity, A=Area | m³/s or CFM | Basic air flow |  | Air Flow (CFM): | 1000
Air Flow | CFM Conversion | CFM = m³/s × 2118.88 |  | CFM | 1 m³/s = 2118.88 CFM |  | Velocity (FPM): | 800
Air Flow | L/s Conversion | L/s = m³/s × 1000 |  | L/s | 1 m³/s = 1000 L/s |  | Duct Area (sq ft): | 0
Air Flow | Required ACH Flow | Q = (V × ACH) / 3600 | V=Volume(m³), ACH=Air Changes/Hour | m³/s | Ventilation sizing |  | Round Duct Dia (inches): | 382.9846
Air Flow | CFM from TR | CFM = TR × 400 | TR=Tons refrigeration | CFM | Rule of thumb: 400 CFM/TR |  | Rect Duct Width (inches): | 24
Cooling Load | Sensible Cooling | Qs = 1.23 × Q × ΔT | Qs=Sensible heat(kW), Q=Flow(m³/s), ΔT=Temp diff(°C) | kW | Air density @ STP |  | Rect Duct Height (inches): | 300.7954
Cooling Load | Latent Cooling | Ql = 3010 × Q × Δω | Ql=Latent heat(kW), Δω=Humidity ratio diff(kg/kg) | kW | Moisture removal
Cooling Load | Total Cooling | Qt = Qs + Ql |  | kW | Sum of sensible + latent |  | HVAC CAPACITY CALCULATOR | 100
Cooling Load | Cooling Tons | TR = Qt / 3.517 | TR=Tons refrigeration | TR | 1 TR = 3.517 kW |  | Room Area (m²): | 3
Cooling Load | Sensible (Imperial) | Qs = 1.08 × CFM × ΔT |  | BTU/hr | CFM in cubic feet/min |  | Room Height (m): | 10
Cooling Load | Latent (Imperial) | Ql = 0.68 × CFM × Δgr | Δgr=Grains moisture/lb | BTU/hr | 7000 grains = 1 lb |  | Occupancy (people): | 120
Heating Load | Heating Load | Qh = 1.23 × Q × ΔT | Qh=Heating load(kW) | kW | Air heating |  | Heat Load (W/m²): | 0.3
Heating Load | Boiler Capacity | Qb = Qh / η | η=Efficiency (0.85-0.95) | kW | Include system losses |  | Total Cooling Load (kW): | 34.12
Fan Power | Fan Power | P = (Q × ΔP) / (1000 × ηfan) | P=Power(kW), ΔP=Pressure(Pa), ηfan=Fan efficiency | kW | Typical ηfan: 0.6-0.8 |  | Required Tonnage (TR): | 0
Fan Power | Fan Total Pressure | ΔPtotal = ΔPstatic + ΔPvelocity | ΔPvelocity = ρv²/2 | Pa | External static + velocity |  | Air Changes/Hour:
Pump Power | Pump Power | P = (ρ × g × Q × H) / (1000 × ηpump) | ρ=Density(kg/m³), g=9.81, H=Head(m) | kW | Water pumping
Pump Power | Pump Head | H = ΔP / (ρ × g) | ΔP=Pressure diff(Pa) | m | Pressure to head conversion
Chiller | Chiller COP | COP = Qc / Wc | Qc=Cooling capacity, Wc=Compressor power | Ratio | Higher is better (3-7)
Chiller | Chiller EER | EER = BTU/hr / Watts |  | BTU/W·hr | Imperial efficiency rating
Chiller | kW/TR | kW/TR = 3.517 / COP |  | kW/TR | Energy per ton, lower better
Chiller | Evaporator Flow | Qw = Qc / (Cpw × ρw × ΔT) | Cpw=4.18 kJ/kg·K, ρw=1000 kg/m³ | m³/s | Chilled water flow
Refrigeration | Refrigerant Mass Flow | mr = Qc / (h1 - h4) | h1, h4=Enthalpies from P-h diagram | kg/s | Vapor compression cycle
Refrigeration | Compression Ratio | CR = Pc / Pe | Pc=Condenser pressure, Pe=Evaporator pressure | Ratio | Affects efficiency
Duct Sizing | Duct Velocity | v = Q / A | A=Cross-sectional area(m²) | m/s | Main: 6-10 m/s, Branch: 4-6 m/s
Duct Sizing | Circular Duct Area | A = π × D² / 4 | D=Diameter(m) | m²
Duct Sizing | Rectangular Equiv Diameter | De = 1.3 × (a × b)^0.625 / (a + b)^0.25 | a, b=Duct sides(mm) | mm | For pressure drop calcs
Duct Pressure Drop | Friction Loss | ΔP = f × (L/D) × (ρv²/2) | f=Friction factor, L=Length, D=Diameter | Pa | Darcy-Weisbach equation
Duct Pressure Drop | Fitting Loss | ΔP = K × (ρv²/2) | K=Loss coefficient | Pa | Bends, tees, dampers
Pipe Sizing | Water Velocity | v = Q / A |  | m/s | CHW: 1-3 m/s, HW: 0.5-2 m/s
Pipe Sizing | Pipe Flow Area | A = π × (ID)² / 4 | ID=Internal diameter | m²
Pipe Pressure Drop | Darcy-Weisbach | ΔP = f × (L/D) × (ρv²/2) |  | Pa | Pipe friction loss
Pipe Pressure Drop | Hazen-Williams | ΔP = 10.67 × Q^1.85 / (C^1.85 × D^4.87) × L | C=Roughness coeff (120-140) | kPa | Water pipes
Ventilation | Fresh Air per Person | Qp = n × Vp | n=Occupants, Vp=L/s per person | L/s | ASHRAE 62.1: 8-10 L/s·person
Ventilation | Ventilation Effectiveness | εv = (Cs - Csup) / (Cex - Csup) | C=Contaminant concentration | Ratio | Mixing: 1.0, Displacement: >1.0
Psychrometrics | Relative Humidity | RH = (Pw / Pws) × 100% | Pw=Partial pressure water, Pws=Saturation pressure | % | From psychrometric chart
Psychrometrics | Humidity Ratio | ω = 0.622 × (Pw / (P - Pw)) | P=Atmospheric pressure | kg/kg | Mass moisture per mass dry air
Psychrometrics | Enthalpy | h = Cpa × T + ω × (hfg + Cpv × T) | Cpa=1.006, hfg=2501, Cpv=1.86 | kJ/kg | Moist air enthalpy
Thermal | Heat Transfer | Q = U × A × ΔT | U=Overall heat transfer coeff(W/m²·K), A=Area(m²) | W | Through surfaces
Thermal | R-Value | R = 1 / U | R=Thermal resistance | m²·K/W | Insulation rating
Efficiency | SEER | SEER = BTU cooling / Wh consumed |  | BTU/Wh | Seasonal energy efficiency
Efficiency | HSPF | HSPF = BTU heating / Wh consumed |  | BTU/Wh | Heating seasonal performance
FLOOR LEVELS
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
B03 | Basement 3 | Third basement level
B02 | Basement 2 | Second basement
B01 | Basement 1 | First basement
LG | Lower Ground | Semi-basement
L00 | Ground Floor | Main entrance
LM | Mezzanine | Intermediate level
L01 | Level 1 | First floor
L02 | Level 2 | Second floor
L03 | Level 3 | Third floor
L04 | Level 4 | Fourth floor
L05 | Level 5 | Fifth floor
L06 | Level 6 | Sixth floor
L07 | Level 7 | Seventh floor
LP | Penthouse | Upper level
LR | Roof | Roof level
ZONE CODES
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
Z01 | Zone 1 | Primary zone
Z02 | Zone 2 | Secondary zone
Z03 | Zone 3 | Tertiary zone
Z04 | Zone 4 | Fourth zone
Z05 | Zone 5 | Fifth zone
COR | Corridor | Circulation areas
EXT | External | Outdoor equipment
PKG | Parking | Parking garage
PLANT | Plant Room | MEP plant room
ROOF | Roof | Roof equipment
SVC | Service | Service areas
UTIL | Utility | Utility rooms
DISCIPLINE CODES - ISO 19650-2
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
C | Controls/BMS | ISO 16484
D | Data/Telecom | ISO/IEC 11801
E | Electrical | IEC 60364
F | Fire Protection | NFPA 13
FA | Fire Alarm | NFPA 72
KIT | Kitchen | NFPA 96
L | Lighting | IEC 60598
LAB | Laboratory | Lab systems
LAU | Laundry | Laundry equipment
M | Mechanical | ASHRAE
MG | Medical Gas | ISO 7396
P | Plumbing | ISO 15874
RE | Renewable | Solar/wind
S | Security | Access/CCTV
VT | Vertical Transport | Elevators
HVAC LOAD CALCULATIONS - COOLING
Calculation Method: ASHRAE Fundamentals (Uganda Climate)
| Fibreglass 25mm | 25mm fiberglass blanket |  | DDC | Direct Digital Control |  | Floor | Floor mounted
Zone/Space | Fibreglass 50mm | 50mm fiberglass blanket | Sensible (kW) | ON/OFF | On/Off control | Tons (TR) | Wall | Wall mounted
Office Open Plan | Armaflex 13mm | 13mm elastomeric foam | 35 | VFD | Variable Frequency Drive | #VALUE! | Ceiling | Ceiling mounted
Meeting Rooms | Armaflex 19mm | 19mm elastomeric foam | 12 | PID | PID Controller | #VALUE! | Roof | Roof mounted
Server Room | Armaflex 25mm | 25mm elastomeric foam | 25 | MOD | Modulating Control | #VALUE! | Suspended | Suspended from structure
Lobby/Reception | Rockwool 50mm | 50mm mineral wool | 15 | 2POS | 2-Position Control | #VALUE! | Ground | Ground level pad
| PIR 40mm | 40mm PIR board |  | 3POS | 3-Position Control | 0 | Recess | Recessed installation
| None | No insulation
MECHANICAL DESIGN CONDITIONS - UGANDA (ISO 19650 COMPLIANT) | Unnamed: 1 | Unnamed: 2 | Unnamed: 3 | Unnamed: 4 | Unnamed: 5
Parameter | Summer | Winter | Units | Notes | Standard
Outdoor Dry Bulb Temp | 30 | 18 | °C | 2.5% design conditions | ASHRAE
Outdoor Wet Bulb Temp | 24 | 15 | °C | 2.5% design conditions | ASHRAE
Indoor Temp - Office | 24 ± 1 | 22 ± 1 | °C | Comfort range | ASHRAE 55
Indoor Temp - Retail | 24 ± 2 | 22 ± 2 | °C | Customer comfort | ASHRAE 55
Indoor Relative Humidity | 50 ± 10 | 40 ± 10 | % | Comfort range | ASHRAE 55
Ventilation Rate - Office | 10 | 10 | L/s/person | Fresh air minimum | ASHRAE 62.1
Ventilation Rate - Meeting | 10 | 10 | L/s/person | Higher occupancy | ASHRAE 62.1
Air Changes - Toilet | 8-10 | 8-10 | ACH | Exhaust only | ASHRAE 62.1
Air Changes - Car Park | 6-10 | 6-10 | ACH | CO monitoring | ASHRAE 62.1
Air Changes - Kitchen | 20-30 | 20-30 | ACH | Make-up air required | ASHRAE
Altitude - Kampala | 1190 | 1190 | m | Above sea level | -
Atmospheric Pressure | 88.3 | 88.3 | kPa | At 1190m altitude | -

## BMS CONTROLS DATA, TELE
BMS CONTROLS, DATA & TELECOMMUNICATIONS |  |  |  | Section 7.2 - SENSORS & TRANSMITTERS per ISO 16484-2 |  |  | Section 7.3 - ACTUATORS per ISO 16484-2 |  |  | Section 7.4 - INTERFACE DEVICES per ISO 16484-2 |  |  | Section 7.5 - NETWORK DEVICES per ISO 16484-5 |  |  | Section 8.1 - STRUCTURED CABLING per ISO/IEC 11801 |  |  | Section 8.2 - ACTIVE NETWORK EQUIPMENT per IEEE 802.3
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE |  | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference | Code | Description | Technical Specification / Standard Reference
BMS POINTS CALCULATOR | Air Flow Controller | Air flow tracking controller |  | AFPS | Air Flow Pressure Sensor | Differential pressure air flow sensor | 2PDACT | 2-Position Damper Actuator | Two-position on/off damper actuator | AIM | Analog Input Module | Multi-channel analog input module | HMI | Human Machine Interface | Operator HMI touchscreen per ISO 16484-3 | 24PP | 24-Port Patch Panel | 24-port Cat5e/Cat6 patch panel | 10GSW | 10-Gigabit Switch | 10GbE network switch per IEEE 802.3ae
Equipment Type | Quantity | Points/Unit | Total Points | AFS | Air Flow Sensor | Air velocity/flow sensor | 2PVACT | 2-Position Valve Actuator | Two-position on/off valve actuator | AOM | Analog Output Module | Multi-channel analog output module | LONGTW | LonWorks Gateway | LonWorks to BACnet gateway | 48PP | 48-Port Patch Panel | 48-port Cat5e/Cat6 patch panel | ACCESS | Access Switch | Access layer switch
AHU | 10 | 25 | 250 | AFSS | Air Flow Switch | Air flow proving switch | 3WVACT | 3-Way Valve Actuator | Three-way mixing valve actuator | BACGTW | BACnet Gateway | BACnet protocol gateway per ISO 16484-5 | MOBGTW | Modbus Gateway | Modbus to BACnet gateway | APPS | Angled Patch Panel | Angled keystone patch panel | AP | Access Point | Wireless access point per IEEE 802.11ax
FCU | 50 | 8 | 400 | COS | CO2 Sensor | Carbon dioxide sensor per ISO 16000-26 | DACT | Damper Actuator | Modulating damper actuator per ISO 16484 | DIM | Digital Input Module | Multi-point digital input module | NAE | Network Automation Engine | Building automation server per ISO 16484 | CM | Cable Manager | Horizontal/vertical cable manager | BRTR | Border Router | Border/edge router
VAV Box | 30 | 6 | 180 | DHS | Duct Humidity Sensor | Duct-mounted RH sensor | MACT | Motor Actuator | General motor actuator | DOM | Digital Output Module | Multi-point digital output module | NCS | Network Control System | Network control system | CPP | Copper Patch Panel | Copper UTP patch panel per ISO/IEC 11801 | CORESW | Core Switch | Core network switch
Chiller | 2 | 45 | 90 | DPS | Differential Pressure Sensor | ΔP transmitter per IEC 61326 | MDACT | Modulating Damper Actuator | Proportional damper actuator 0-10V/4-20mA | EXM | Expansion Module | Controller I/O expansion module | OWS | Operator Workstation | BAS operator workstation | DDO | Double Data Outlet | Dual-port RJ45 outlet | DISTSW | Distribution Switch | Distribution layer switch
Pump | 8 | 5 | 40 | DTS | Duct Temperature Sensor | Duct air temperature sensor | MVACT | Modulating Valve Actuator | Proportional valve actuator 0-10V/4-20mA | GTW | Gateway | Protocol conversion gateway | PWS | Portable Workstation | Portable commissioning workstation | DO | Data Outlet | Single RJ45 data outlet per ISO/IEC 11801-1 | EAP | External Access Point | Outdoor wireless AP
Temperature Sensor | 100 | 1 | 100 | HS | Humidity Sensor | Relative humidity sensor | ROACT | Rotary Actuator | Rotary valve/damper actuator | IOEXP | I/O Expansion | Input/output expansion module |  |  |  | FO | Fiber Outlet | Fiber optic wall outlet | ERTR | Edge Router | Edge router
Pressure Sensor | 20 | 1 | 20 | ITS | Immersion Temperature Sensor | Immersion/well temperature sensor | SRDACT | Spring Return Damper Actuator | Fail-safe spring return actuator | RMOD | Relay Output Module | Multi-relay output module |  |  |  | FPCC | Front Panel Cable Cover | Patch panel cable management cover | GESW | Gigabit Ethernet Switch | 1GbE switch per IEEE 802.3ab
Flow Meter | 15 | 2 | 30 | OTS | Outdoor Temperature Sensor | Outdoor ambient temperature sensor | VACT | Valve Actuator | Control valve actuator per ISO 16484 | UIM | Universal Input Module | Configurable universal input module |  |  |  | FPP | Fiber Patch Panel | Fiber optic patch panel LC/SC per ISO/IEC 11801-2 | IAP | Indoor Access Point | Indoor ceiling/wall AP
UAC | Unitary Application Controller | Equipment-level unitary controller |  | PMS | Particulate Matter Sensor | PM2.5/PM10 air quality sensor | [9 empty] | HCM | Horizontal Cable Manager | Horizontal cable management | MESH | Mesh Access Point | Wireless mesh AP
Total BMS Points: | VAV Box Controller | VAV terminal unit controller per ASHRAE 135 | 1110 | PS | Pressure Sensor | Absolute/gauge pressure transmitter | [9 empty] | PP | Patch Panel | General patch panel | NSW | Network Switch | Managed network switch
Controllers Required (50 pts/controller): |  |  | 23 | RHS | Room Humidity Sensor | Room relative humidity sensor | [9 empty] | QDO | Quad Data Outlet | Quad-port RJ45 outlet | POESW | PoE Switch | Power over Ethernet switch per IEEE 802.3af/at/bt
|  |  |  | RTS | Room Temperature Sensor | Room temperature sensor per ISO 7730 | [9 empty] | SDO | Single Data Outlet | Single-port data outlet | RTR | Router | Network router
|  |  |  | THS | Temperature/Humidity Sensor | Combined temp/RH sensor | [9 empty] | VCM | Vertical Cable Manager | Vertical cable management system | WAP | Wall Access Point | Wall-mounted wireless AP
|  |  |  | TS | Temperature Sensor | Temperature transmitter per IEC 60751 | [12 empty] | WLRTR | Wireless Router | Integrated wireless router
|  |  |  | VOCS | VOC Sensor | Volatile organic compound sensor
PLANTC | Plant Controller | Central plant optimization controller |  | WFS | Water Flow Sensor | Water flow meter/sensor
ZONEC | Zone Controller | Zone-level temperature/HVAC controller |  | WFSS | Water Flow Switch | Water flow proving switch
LIGHTC | Lighting Controller | Lighting control system per ISO 16484-2 |  | WPS | Water Pressure Sensor | Water pressure transmitter
ENERGYC | Energy Controller | Energy management controller
CTS | Chilled Water Temp Sensor | CHW supply/return temperature sensor
HTS | Hot Water Temp Sensor | HW supply/return temperature sensor
PRESSS | Pressure Sensor | Differential pressure sensor
FLOWS | Flow Sensor | Water/air flow sensor
POWERM | Power Meter | Energy/power monitoring meter
CO2S | CO2 Sensor | Carbon dioxide sensor for IAQ
VOQS | VOC Sensor | Volatile organic compound sensor
MVALVE | Motorized Valve | Motorized control valve 2/3-way
BVALVE | Ball Valve Actuator | Actuated ball valve
DAMPER | Damper Actuator | Motorized damper actuator
ROUTER | Network Router | BACnet/IP router per ISO 16484-5
MSTP | MS/TP Network | BACnet MS/TP network per ISO 16484-5
GATEWAY | Protocol Gateway | Multi-protocol gateway device

## FIRE PROTECTION-NFPA
NFPA 72/13 - FIRE PROTECTION & ALARM SYSTEMS |  |  |  | MANUAL DEVICES |  |  | NOTIFICATION DEVICES |  |  | CONTROL EQUIPMENT
|  |  |  | Code | Description | Standard / Specification | Code | Description | Standard / Specification | Code | Description | Standard / Specification
FIRE ALARM DEVICE CALCULATOR |  |  | SPRINKLER DESIGN PARAMETERS | ADDR | Addressable Manual | Addressable pull | BCON | Beacon | Visual beacon | ANN | Annunciator | Remote annunciator
Building Area (m²): | 5000 | Standard / Specification | Hazard Classification: | Ordinary Hazard Group 1 | Break Glass | Break glass | BEL | Bell | Alarm bell | CFACP | Conventional FACP | Conventional panel
Number of Floors: | 3 | Addressable analog | Design Density (mm/min): | 6.1 | Manual Call Point | Manual alarm | BSTB | Bell/Strobe | Combined | FACP | Fire Alarm Panel | Main panel
Smoke Detectors Required: | 188 | Air sampling | Design Area (m²): | 140 | Pull Station | Pull station | HORN | Horn | Alarm horn | IOMOD | I/O Module | Input/output
Heat Detectors Required: | 125 | Projected beam | Sprinkler Spacing (m): | 4.6 | Reset Point | System reset | HSTB | Horn/Strobe | Combined | ISOMOD | Isolation Module | Isolator
Manual Call Points: | 38 | Combined detector | Water Flow Required (L/min): | 854 | Test Point | System test | LED | LED Indicator | LED status | MON | Monitor Module | Supervisory
Notification Devices: | 75 | Carbon dioxide | Number of Sprinklers: | 7 |  |  | SIREN | Siren | Alarm siren | NFACP | Network FACP | Networked panel
Total Loop Loading: | 426 | Carbon monoxide |  |  |  |  | STB | Strobe | Visual strobe | RANN | Remote Annunciator | Remote display
DSD | Duct Smoke Detector | HVAC duct |  |  |  |  | TONE | Tone Generator | Audible tone | RMOD | Relay Module | Control relay
FHD | Fixed Temp Heat | Fixed temperature |  |  |  |  | VSA | Visual/Sounder | Combined | RP | Repeater Panel | Signal repeater
GD | Gas Detector | Combustible gas
HD | Heat Detector | General heat
INTDET | Intelligent Detector | Addressable
ISD | Ionization Smoke | Ionization type
LHD | Linear Heat | Linear detection
MSD | Multi-Sensor | Combined
PSD | Photoelectric Smoke | Photoelectric
RHD | Rate-of-Rise Heat | ROR type
SD | Smoke Detector | General smoke
SPRINKLER HEADS - NFPA 13
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
PEN | Pendent Sprinkler | Standard spray pendent per NFPA 13
UPR | Upright Sprinkler | Standard spray upright
SW | Sidewall Sprinkler | Sidewall spray head
CWSS | Concealed Sprinkler | Flush concealed pendent
ESFR | ESFR Sprinkler | Early Suppression Fast Response
DRYSP | Dry Sprinkler | Dry pendant for cold areas
FIRE PUMPS & EQUIPMENT - NFPA 20
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
FPUMP | Fire Pump | Electric/diesel fire pump per NFPA 20
JOCKP | Jockey Pump | Pressure maintenance pump
RISER | Fire Riser | Vertical fire main
FHC | Fire Hose Cabinet | Hose reel cabinet per NFPA 14
FHYDR | Fire Hydrant | External fire hydrant
FDC | Fire Dept Connection | Siamese fire department connection
FIRE SUPPRESSION - NFPA 2001 / FM-200
ASSETMANAGEMENT_PRODUCT_CODE | PROJECTINFO_DESCRIPTION_TXT | REGULATORY_UNBS_STANDARD_REFERENCE
FM200 | FM-200 System | Clean agent suppression per NFPA 2001
CO2SUP | CO2 Suppression | Carbon dioxide suppression
FESUP | Fire Extinguisher | Portable extinguisher per NFPA 10
KITSP | Kitchen Suppression | Kitchen hood suppression NFPA 17A